March 1, 2026

Mr. Brad Vifquain

Hanover Insurance

440 Lincoln St

Worcester, MA 01615

| RE: | Insured: | PASTEUR PLAZA SURGERY CENTER |
| --- | --- | --- |
|  | Claim Number: LSG Matter Number: Date of Loss: | 85-00915163 426600.4187-00 January 26, 2026 |

Dear Mr. Vifquain,

Thank you for choosing Loss Solutions Group as your equipment loss consultant.  This report serves to provide an analysis of the above-referenced claim.

Assignment:

Loss Solutions Group was contacted by Mr. Brad Vifquain of Hanover Insurance. The scope of this assignment was to address the evaporator water coil for a Trane packaged rooftop air conditioning unit located at Pasteur Plaza Surgery Center, 7909 Fredericksburg Rd Ste 222, San Antonio, TX 78229. The unit reportedly sustained damage as a result of cold weather/freeze-up conditions on or about January 26, 2026, during Winter Storm Fern.

Findings and Analysis:

Loss Solutions Group contacted the insured, Ms. Laura Rodrick of Pasteur Plaza Surgery Center, at (210) 614-4544 x1991. Ms. Rodrick reported that it got very cold in the San Antonio area and the rooftop unit stopped working. She stated that Trane came out to the location and found that the evaporator water coil had burst. She noted that the unit is large and a crane would be needed for the replacement. She further reported that the unit has been repaired and is back up and running. Ms. Rodrick estimated the unit to be from approximately 2001.

Loss Solutions Group contacted the vendor, Mr. Chris Ust, Account Manager with Trane US Inc., at (726) 205-9127. Mr. Ust confirmed the scope of the repairs and provided a breakdown of costs. He reported that the work involved four technicians over two full days, with crane support for both days. The scope included the custom-made evaporator water coil, welding, dielectric fittings, and various other materials needed to complete the installation. Mr. Ust confirmed the coil specifications and described it as having copper tubes with aluminum fins and a galvanized steel casing. He also confirmed the applicable sales tax rate of 8.25%.

Loss Solutions Group contacted Coil Replacement Company at (866) 297-0558. Mr. Adrian Kniahynycky, Sales Engineer, provided a quote for a custom-built chilled water coil matching the specifications of the damaged unit.

A total amount of $32,998.54 (excluding applicable sales tax) was presented.

Scope of Damage

On or about January 26, 2026, the evaporator water coil within a Trane packaged rooftop air conditioning unit (Model: TSCA012U0A, Serial: K01L59818C) at Pasteur Plaza Surgery Center reportedly sustained damage as a result of cold weather/freeze-up conditions during Winter Storm Fern. Photos provided show burst copper U-bends on the chilled water coil.

Age & Condition

Based on information gathered during the investigation, the Trane packaged rooftop air conditioning unit was manufactured in approximately 2001, making it roughly twenty-five (25) years old at the time of loss. The equipment nameplate information had faded due to prolonged sun exposure. Based on its age, the unit was in average condition at the time of loss.

Cause of Loss

The evaporator water coil reportedly sustained damage as a result of cold weather/freeze-up conditions during the 2026 Winter Storm Fern event on or about January 26, 2026. The freezing temperatures caused the water within the coil to expand, resulting in burst copper tubing. Photos provided support the reported cause of loss, showing split and burst copper U-bends consistent with freeze damage.

Reparability

Due to the nature and extent of the damage to the evaporator water coil, replacement of the coil was deemed necessary. The coil was not a candidate for repair, as the burst copper tubing throughout the coil rendered it beyond economical repair. The unit has since been repaired with a new evaporator water coil installed by Trane US Inc.

Cost Analysis

TRANE US INC. (210-657-0901) PROPOSAL ID: 8564210

Trane US Inc. submitted Proposal ID 8564210 in the total amount of $32,998.54 (excluding applicable sales tax) for the replacement of the evaporator water coil on the Trane packaged rooftop air conditioning unit. The proposal included the custom evaporator water coil, other materials (dielectric fittings, welding materials, nitrogen gas, brazing rods, etc.), labor for four technicians over two full days, crane rental for two days, and truck trip charges. The work was performed after hours as required due to the surgery center's operations.

Loss Solutions Group researched the cost of the evaporator water coil through Coil Replacement Company, who provided a quote of $7,457.00 for a custom-built chilled water coil matching the specifications of the damaged unit. With the addition of approximately $1,000.00 for shipping and handling and a 30% vendor markup on materials, the researched coil cost totals approximately $11,000.00.

Loss Solutions Group broke down Trane's lump sum proposal into its component costs. The remaining balance of $3,398.54 was allocated to other materials including dielectric fittings, welding materials, nitrogen gas, brazing rods, and similar items. Labor was calculated at 64 hours (four technicians for two full days) at $250.00 per hour, totaling $16,000.00. Crane rental was calculated at $1,200.00 per day for two days, totaling $2,400.00. Truck trip charges were calculated at $50.00 per vehicle for four technician vehicles, totaling $200.00.

The costs presented are considered fair and reasonable for the scope of work performed. Please refer to the attached spreadsheet for a detailed breakdown.

Replacement Cost Value (RCV)

Based on Loss Solutions Group's research and analysis, the total Replacement Cost Value (RCV) for this claimed event is $35,720.92, inclusive of 8.25% sales tax. Please refer to the attached spreadsheet for a detailed cost breakdown.

Actual Cash Value (ACV)

The equipment was manufactured in approximately 2001, making it roughly twenty-five (25) years old at the time of loss. For depreciation purposes, the evaporator water coil and other materials carry a useful life expectancy of twenty (20) years. Given the equipment's age of twenty-five (25) years exceeds the useful life of twenty (20) years, the depreciation percentage is capped at the maximum of seventy-five percent (75%). Labor, crane, and truck trip charges are not subject to depreciation.

Based on the above, the total Actual Cash Value (ACV) for this claimed event is $24,031.10. Please refer to the attached spreadsheet for a detailed breakdown.

Salvage

Loss Solutions Group submits that there is little to no salvage value associated with this claimed event.

- Summary:

- Loss Solutions Group's findings herein are based upon all information that was available at the time of this writing. The opinions are based upon reviewed documentation, interviews, research, experience, historical references, training and education.

- Pasteur Plaza Surgery Center sustained damage to an evaporator water coil within a Trane packaged rooftop air conditioning unit as a result of reported cold weather/freeze-up conditions during Winter Storm Fern on or about January 26, 2026. A total amount of $32,998.54 (excluding sales tax) was presented by Trane US Inc.

- The Trane unit was manufactured in approximately 2001 and was in average condition at the time of loss.

- The Replacement Cost Value (RCV) is $35,720.92.

- The Actual Cash Value (ACV) is $24,031.10.

- Loss Solutions Group submits that there is little to no salvage value associated with this claimed event.

Should you require any additional information, please don't hesitate to contact me at (866) 899-8756, ext 755, or by email at tbeuret@losssolutionsgroup.com. For any immediate concerns, feel free to contact Team Leader Nick Ramos at (866) 899-8756, ext 724, or by email at nramos@losssolutionsgroup.com.

Best regards,

| Tanner Beuret Technical Consultant Loss Solutions Group, LLC |  |
| --- | --- |