February 7, 2026

Ms. Teri Tucker

Hanover Insurance

PO Box 15147

Worcester, MA 01615

| RE: | Insured: | Spare Time Inc. |
| --- | --- | --- |
|  | Claim Number: LSG Matter Number: Date of Loss: | 85-00900748 426600.4163-00 December 26, 2025 |

Dear Ms. Tucker,

Thank you for choosing Loss Solutions Group as your equipment loss consultant. This report provides an analysis of the above-referenced claim.

Assignment:

Loss Solutions Group was contacted by Ms. Teri Tucker of Hanover Insurance. The scope of this assignment was to assess the extent of damage and salvage value associated with the insured’s one (1) Trane-branded ten (10) ton packaged HVAC unit, one (1) American Standard ten (10) ton packaged HVAC unit, and one (1) Febco-branded rear backflow device—all sustaining damage during a vandalism/theft event on December 26, 2025.

Findings and Analysis:

Loss Solutions Group contacted the insured, Mr. Chris Vandyke, with Spare Time Inc. (209-371-9839), to discuss his role in the claim. Mr. Vandyke explained how vandals gained access to his ground-mounted packaged HVAC units and stripped them of their valuable components. Fortunately, one of the units, a Trane-branded model (RTU 1-C), was reported to be repairable. He noted that this was the second vandalism incident in just a few days, as vandals had damaged two other Trane-branded units two days prior. Additionally, Mr. Vandyke mentioned that the main water backflow valve located at the rear also sustained damage, as the vandals cut the stem of the brass valve, necessitating further repairs.

Loss Solutions Group contacted the insured’s HVAC vendor, Iron Mechanical (916-347-6292), and spoke with Mr. Michael Dobkin to discuss the claimed event and their repairs. Mr. Dobkin explained that they found one unit damaged beyond repair, one unit requiring compressor replacements alongside other repairs, and a backflow preventer needing new stems to ensure proper operation.

A total amount of $52,821.00 was presented.

Scope of Damage

Loss Solutions Group submits that the insured’s one (1) Trane-branded ten (10) ton packaged HVAC unit, one (1) American Standard ten (10) ton packaged HVAC unit, and one (1) Febco-branded rear backflow device—all sustaining damage during a vandalism/theft event on December 26, 2025.

Age & Condition

The insured reported that the affected equipment varied in age: the Trane-branded HVAC unit is twenty (20) years old, the Febco backflow preventer is also twenty (20) years old, and the American Standard unit is fifteen (15) years old. At the time of the reported event, all equipment was said to be in average condition.

Cost Analysis

Loss Solutions Group assessed the proposed costs by cross-referencing with alternative vendors, drawing on historical data for similar repairs, evaluating comparable equipment pricing, and consulting directly with the involved vendor to verify reasonableness.

IRON MECHANICAL (916-347-6292) ESTIMATE # 26-SP-008 (REPLACEMENT OF RTU 1-E)

Loss Solutions Group reviewed the first proposal presented by Iron Mechanical, totaling $35,320.00 for the replacement of one (1) packaged unit.

Included in the cost is an amount for one (1) replacement in-kind ten (10) ton Bryant packaged unit, high voltage electrical equipment, gas piping connections, thermostat wiring, and a condensation drain line. We submit that these components are required to complete the replacement, and the costs are fair and reasonable.

Loss Solutions Group has reviewed the labor costs for the vendor to diagnose the damage and to perform the replacement, along with their travel expenses. We submit that these amounts are fair and reasonable to complete the scope of work as presented to us.

Note: The vendor decided to replace the Trane-branded unit with a Bryant-branded unit. Both brands are produced by Carrier Global Corporation in the same manufacturing facilities and share many interchangeable internal components. Since Bryant is comparable in quality to Trane, we do not expect a significant price difference between the two brands.

IRON MECHANICAL (916-347-6292) ESTIMATE # 1008251658 (REPAIR TO RTU 1-C)

Loss Solutions Group reviewed the second proposal presented by Iron Mechanical, totaling $11,556.00 for the repairs to one Trane ten (10) ton unit.

Included in the cost is an amount for two (2) Trane-branded scroll compressors, compressor electrical harnesses, two (2) liquid line refrigerant dryers, roughly fifteen (15) pounds of R 407A refrigerant, suction and discharge line piping repairs, along with one refrigerant line flushing kit to remove all non-condensables. We submit that these components are required to complete the repair, and the costs are fair and reasonable.

Loss Solutions Group has reviewed the labor costs for the vendor to diagnose the damage and to perform the repairs. We submit that these amounts are fair and reasonable to complete the scope of work as presented to us.

IRON MECHANICAL (916-347-6292) ESTIMATE # 1008251689 (BACKFLOW REPAIR)

Loss Solutions Group reviewed the third proposal presented by Iron Mechanical, totaling $5,945.00 for repairs to the Febco eight (8) inch backflow preventer unit located in the rear.

Included in the cost is an amount for two (2) replacement stainless steel threaded stems for the two large valves. We submit that these components are required to complete the repair, and the costs are fair and reasonable.

Loss Solutions Group has reviewed the labor costs for the vendor to diagnose the damage and to perform the repairs. We submit that these amounts are fair and reasonable to complete the scope of work as presented to us.

RCV

Loss Solutions Group submits an amount of $52,821.00 (RCV) as being fair and reasonable to return the insured to a pre-loss condition. A further breakdown of the pricing is available in the attached spreadsheet.

ACV

Loss Solutions Group submits an actual cash value (ACV) amount of $24,409.50 based on linear age depreciation of the materials only. We estimate the average life expectancy of the equipment to be around twenty (20) years.

Salvage

Loss Solutions Group submits that there is little to no salvage value associated with this claimed event.

Summary:

Loss Solutions Group’s findings herein are based upon all information that was available at the time of this writing.  The opinions are based upon reviewed documentation, interviews, research, experience, historical references, training and education.

- The insured, Spare Time Inc, claimed that their one (1) Trane-branded ten (10) ton packaged HVAC unit, one (1) American Standard ten (10) ton packaged HVAC unit, and one (1) Febco-branded rear backflow device—all sustaining damage during a vandalism/theft event on December 26, 2025. A total amount of $52,821.00 was presented.

- The insured reported that the affected equipment varied in age: the Trane-branded HVAC unit is twenty (20) years old, the Febco backflow preventer is also twenty (20) years old, and the American Standard unit is fifteen (15) years old. At the time of the reported event, all equipment was said to be in average condition.

- Loss Solutions Group submits an amount of $52,821.00 (RCV) as being fair and reasonable to return the insured to a pre-loss condition. A further breakdown of the pricing is available in the attached spreadsheet.

- Loss Solutions Group submits an actual cash value (ACV) amount of $24,409.50 based on linear age depreciation of the materials only.

- Loss Solutions Group submits that there is little to no salvage value associated with this claimed event.

If you have any questions or if you need any additional information, please feel free to contact Tanner Beuret at (866) 899-8756 ext. 755, or via email at tbeuret@losssolutionsgroup.com.  Team Leader Nick Ramos can be reached at (866) 899-8756 ext. 724, or via email at nramos@losssolutionsgroup.com.

Best regards,

| Tanner Beuret Technical Consultant Loss Solutions Group, LLC |  |
| --- | --- |