November 7, 2025

Mr. Eric Chudzinski

Travelers Insurance

PO Box 430

Buffalo, NY 14240-0430

| RE: | Insured: Claimant: | Bay Crane Service TP Mechanical |
| --- | --- | --- |
|  | Claim Number: LSG Matter Number: Date of Loss: | F2X2280 787200.12584-00 April 15, 2025 |

Dear Mr. Chudzinski,

Thank you for choosing Loss Solutions Group as your equipment loss consultant. This report provides an analysis of the above-referenced claim.

Assignment:

Loss Solutions Group was contacted by Mr. Eric Chudzinski of Travelers Insurance. The scope of this assignment is to evaluate the extent of damages, repair and replacement costs, and (any) salvage value associated with the claimant’s (TP Mechanical) Motivair brand MCDU-40 cooling distribution unit (CDU) stemming from a transit incident on April 15, 2025.

Findings and Analysis:

Loss Solutions Group contacted the insured, Ms. Lauren Newlin, Safety Compliance & Claims Manager of Bay Crane Service (267-462-4506), to explain our role in the claims review. Ms. Newlin confirmed that Bay Crane Service operated the forklift that caused the damages. She indicated she had limited knowledge of the equipment specifications and damage assessment and referred Loss Solutions Group to the equipment vendor, Texas Air Systems, for official unit and damage assessment.

Loss Solutions Group contacted the claimant and general contractor, Mr. Brad Williams, Project Manager of TP Mechanical (859-905-7482) to discuss the reported incident. Mr. Williams explained that TP Mechanical hired Bay Crane Service to perform rigging work for the installation of CDUs at a data center facility. He confirmed that Bay Crane Service's operators were handling the equipment when the damages occurred but indicated he had little information about the extent of damage or equipment specifications.

Loss Solutions Group contacted Mr. Jon Grennell, Project Manager of Bay Crane Midwest (614-753-5881), the division of Bay Crane Service whose operator reportedly caused the incident. Mr. Grennell provided details about the incident and confirmed the circumstances described in Bay Crane Service's Forklift Incident Investigation Report. The Bay Crane Service Forklift Incident Investigation Report documents that On April 15, 2025, at approximately 8:00 AM, as an operator was unloading the CDU from a truck the rear wheel struck a pothole causing the top-heavy unit to slide off the forks and fall onto its side.

Loss Solutions Group contacted the equipment vendor, Texas Air Systems (214-483-1717), and spoke with Ms. Reagan Guthrie regarding the damaged unit and damage assessment. Ms. Guthrie confirmed that Texas Air Systems sold the Motivair MCDU-40 unit to QTS (the equipment owner) for $108,200.00 on February 26, 2024, for installation at QTS's datacenter facility as part of critical cooling infrastructure. Following the incident, Texas Air Systems dispatched technicians to the site to assess the damage. Ms. Guthrie explained that the nature and extent of damages to the unit necessitated Texas Air Systems to consult with the OEM, Motivair, to obtain an official assessment of reparability. Motivair provided a document stating that the unit was non-reparable (explained below in more detail). After speaking with the manufacturer, Motivair, who provided the M.S.R.P. of $94,380.05 for an identical unit, we followed up with Ms. Guthrie to address the $13,819.95 price difference between the M.S.R.P. and their original sale price. She was unable to explain where the added costs came from. She stated that we should speak with the customer regarding their prices.

On October 24, 2025, Ms. Guthrie provided Loss Solutions Group with Motivair's official Damage Assessment Letter. The manufacturer (Motivair) identified multiple categories of damage rendering the unit unrepairable, indicating the structural integrity of the frame, heat exchanger, pumps, valves, and piping was destroyed. Motivair noted this is particularly critical given that this equipment serves in datacenters where structural integrity is essential for reliable operation. Motivair further indicated that all electrical components must be discarded per the supplier's drop-impact policy. In the Damage Assessment Letter, Motivair also noted that due to the damage sustained on impact, electrical and leak testing components were destroyed, and as a result, the unit can no longer be certified for safe operation. Based on these findings, Motivair concluded that complete replacement of the product is required to meet original specifications and quality standards.

A total replacement cost of $108,200.00 was presented.

Scope of Damage

Loss Solutions Group submits that the claimant's Motivair brand MCDU-40 cooling distribution unit sustained extensive internal and external damage stemming from a reported transit incident on April 15, 2025.

Age & Condition

The affected equipment was new and unused at the time of the claimed event.

Reparability

After reviewing the relevant documentation and photographs and consulting with the vendor, Loss Solutions Group concurs that the full replacement of the affected equipment is required to achieve a pre-loss condition.

Cost Analysis

Loss Solutions Group assessed the proposed costs by cross-referencing with alternative vendors, drawing on historical data for similar repairs, evaluating comparable equipment pricing, and consulting directly with the involved vendor to verify reasonableness. Below is a breakdown of the associated costs.

TEXAS AIR SYSTEMS (214-483-1717) INVOICE WITH SHIP DATE FEBRUARY 26, 2024 AND A TOTAL OF $108,200.00

Loss Solutions Group reviewed the invoice totaling $108,200.00 for one (1) Motivair brand MCDU-40 cooling distribution unit. Loss Solutions Group cross-checked with the OEM, Motivair, and found that the MSRP for a like-for-like CDU unit would cost $94,380.05. Loss Solutions Group submits that the OEM cost presented is fair and reasonable to restore the claimant to pre-loss condition.

Note: A difference was noted between the claim cost and Loss Solutions Group’s researched cost, totaling $13,819.95. The difference is attributed to added costs from the vendor above MSRP that the vendor was unable to substantiate.

Alternate Vendor Contacts

Further research to establish valuation utilizing third-party vendors is discussed below.

Motivair by Schneider Electric (716-691-9222 ext 361)

Loss Solutions Group spoke with Nicholas Haddad, Sales Manager, IT & Electronics Cooling of Motivair, who supplied an M.S.R.P. for an identical Cooling Distribution Unit (CDU) in the amount of $94,380.05. Loss Solutions Group submits that the $94,380.05 is consistent with industry standards and deems this price to be fair and reasonable to return the claimant to a pre-loss state.

RCV

Loss Solutions Group submits an amount of $94,380.05 (RCV) as fair and reasonable to return the claimant to a pre-loss condition. A further breakdown of the pricing is available in the attached spreadsheet.

ACV

Loss Solutions Group has not completed an Actual Cash Value (ACV) analysis for the claimed event, as the equipment was in new and unused condition.

Salvage

Loss Solutions Group submits that there is little to no salvage value associated with this claimed event.

Summary:

Loss Solutions Group's findings described herein are based upon all information available at the time of this writing. Loss Solutions Group's findings are based on available information, reviewed documentation, interviews, research, experience, historical references, training, and education.

- The insured, Bay Crane Service, reported damage to a Motivair brand MCDU-40 cooling distribution unit stemming from a transit incident on April 15, 2025, for a total of $108,200.00.

- The affected equipment was new and unused at the time of the claimed event.

- After reviewing the relevant documentation and photographs and consulting with the vendor, Loss Solutions Group concurs that the full replacement of the affected equipment is required to achieve a pre-loss condition.

- Loss Solutions Group submits an amount of $94,380.05 (RCV) as fair and reasonable to return the claimant to pre-loss condition. A further breakdown of the pricing is available in the attached spreadsheet.

  - A difference was noted between the claim cost and Loss Solutions Group’s researched cost, totaling $13,819.95. The difference is attributed to added costs from the vendor above MSRP that the vendor was unable to substantiate.

- Loss Solutions Group has not completed an Actual Cash Value (ACV) analysis for the claimed event, as the equipment was in new and unused condition.

- Loss Solutions Group submits that there is little to no salvage value associated with this claimed event.

If you have any questions or if you need any additional information, please feel free to contact Tanner Beuret at (866) 899-8756 ext. 755, or via email at tbeuret@losssolutionsgroup.com.  Team Leader Nick Ramos can be reached at (866) 899-8756 ext. 724, or via email at nramos@losssolutionsgroup.com.

Best regards,

| Tanner Beuret Technical Consultant Loss Solutions Group, LLC |  |
| --- | --- |